## Power detailed Checklist
Power Audit Performa (iON)
Center name: Center code: Date of audit:
Node capacity: Transformer rating( KVA): Sanctioned load:
No. of DG: Starting: Auto/Manual kva rating: Make:
No. of UPS : Connection: Parallel/Single kva rating: Make:
No. of UPS battery: Voltage & AH value: Make: Manufacuting year:
Equipment/Checks | Tools | Lower limit | Upper limit | Status/Value
Check Tranformer for any abnormality | Visual | Availability of fencing/No trees around /Blue colour of silica gel /No oil leakage
Check Earth Pit | Visual | No break in earthing wire/ metal strip, wet earth pit | Intact
Mains Supply/ LT panel checks
Check all panels are properly closed | Visual | Check wire entry points/front & back covers of panels
Check rubber mat for LT panels & UPS | Visual | Industrial grade rubber mat in front of LT panel & UPS
Chech condition of cable lugs/joints | Visual | Check black marks/sparking/burning smell
Input Voltage(Phase to Neutral Value) | LT panel | 200 V | 240 V
Electrical Frequency | LT panel | 49 Hz | 51 Hz
Phase R, Y, B load ( all equipment on) | LT panel | To ensure 10 – 15 % between phases
load in KVA ( all equipment on) | LT panel | NA | 80%
Main supply availability at center | VH | Regular supply/Interrupting supply
DG checks in stop condition checks
Provision for connecting mobile DG | Visual | Check provision for mobile DG connection
Check DG surroundings/bottom clean | Visual | Check surroundings are clear for air & exhaust flow
DG Starting Battery voltage | DG panel | 11.8 V | 13.5 V
Fuel Level in Tank | DG panel | NA | 90 % before exam day
Check coolant level | Visual | 70% | 90%
Lubricating oil level | Dipstick | Between low and high level mark of dip stick
Check DG belt condition | Visual | No oil/water on belt, no cracks on belt
DG Earthing checks | Visual | No break in earthing wire/ metal strip, wet earth pit
DG running checks
Check DG auto starting | Panel | If auto starting provision available
DG Voltage (Phase to Neutral ) | DG panel | 200 V | 240 V
Electrical Frequency | DG panel | 49 Hz | 51 Hz
DG load in KVA ( load checks for 15 min with all equipment on) | DG panel | 50 % load | 80 % load
Load (R Y B) in Amps or % | DG panel | To ensure 10 – 15 % between phases
Fuel / Lub oil/ Coolant leakage | Visual | No leakage
Lube Oil Pressure | DG panel | 4 bar | 7 bar
Coolant temperature | DG panel | 40 C | 85 C ( alarm) & 90 C (Trip)
Check Exhaust Gases colour | Visual | Exhaust should not to be in black color
UPS Equipment
Input Voltage (Phase to Neutral) | UPS panel | 200 V | 240 V
Output Voltage (Phase to Neutral ) | UPS panel | 200 V | 240 V
Electrical Frequency | UPS panel | 49 Hz | 51 Hz
Lload on Phase (R Y B) in Amps or % ( all equipment on) | UPS panel | To ensure 10 – 15 % between phases
load on UPS in KVA ( all equipment on) | UPS panel |  | 80%
Earth to Neutral Voltage | Multimetr | 0 V | 2 V
UPS Battery Charging in % | UPS panel | 90% | 100%
UPS backup time in minutes | UPS panel | 15 min. | Check batteries if low backup
Check UPS bypass provision availability | Visual | If no provision, keep thimbled wires for bypassing
Check UPS fans working and dust free | Visual | No abnormal noise from Fans
UPS Room temperature | Thermome | 23 C | 25 C
Check dedicated earthing of UPS | Visual | Check earthing of UPS
Check MCBs not overloaded | clampmet |  | 80%
Battery System
Check UPS batteries for Acid marks or Bulging | Inspection | No acid leak or bulging indications
Check MCB/MCCB fitted for supply from Batteries to UPS | Visual | MCB/MCCB should be of correct as per UPS kva rating.
Check voltage of batterries | Multimete | 13 V | 13.5 V
Room Temperature | Inspection | 23 C | 25 C
Equipment functionality checks
Process - Switch on all Desktops, server, A/C, Fan, Lights etc., Put DG in manual mode, cut-off main supply, check UPS changed to battery mode and no PC / MCB tripped, check battery draining rate for 10 minutes, put DG starting in auto mode and check DG started, check power supply from DG to UPS restored, check all Destops/ MCB for any failure, switch on main supply and check DG shutdown, check UPS for main supply availability and all parameters.
Maintenance Records checks
Last UPS maintenance date | records | Quarterly checks should be done
Last UPS Battery maintenance date | records | Quarterly checks should be done
Last DG maintenance date | records | Quarterly checks should be done
Last AC maintenance date | records | Quarterly checks should be done
Letter to EB for uninterrupted supply power supply (for IDZ only) | records | check letter for latest exam
Check EB meter reading register for entry of daily readings (for IDZ only) | records | Daily readings with VH signature
Check electrician ,tools and spares
Check knowledge of electrician | Viva | certified electrician should be available
Check availaility of tools | Tool kit ( multimeter, clamp meter, screw drivers, plier and adjustable spanner)
Check availability of spares | DG spares ( coolant, lub oil, belt, fuse, spare battery wire)
MCBs of 16 amps and above capacity ( one each)
Spare wires for emergency connections
VH Name: Ph no: Signature:
Electrician Name: Ph no: Signature:
TCA Name: Ph no: Signature
Auditor Name: Ph no: Signature:
Auditor Observations:
Validator Name: Vikram/Amit Center Stamp:
Observations status (to be updated by VH):